## Sheet1
# | Test Case | Expect Result | Result | Comments
1 | Manually create an audit, validate a cable | The cable audit status is changed to Verified | Pass
2 | Manually create an audit, validate all cables | All cables are changed to Verified in the list | Pass
3 | Manually create an audit, create a cable | The cable is created with Verified - New status, the rackmount device and the rack of this cable is changed to Verified - Error status, the audit status is changed to Completed With Error | Pass
4 | Manually create an audit, set a cable to Absent | The cable is changed to Absent status, the rackmount device and the rack of this cable is changed to Verified - Error status, the audit status is changed to Completed With Error
5 | Manually create an audit, validate a device without cables | The device audit status is changed to Verified | Pass
6 | Manually create an audit, validate a device with cables not validated | The device cannot be validated before the cables are validated | Pass
7 | Manually create an audit, validate a device with all cables validated | The device audit status is changed to Verified | Pass
8 | Manually create an audit, create a device | The device is created with Verified - New status, the rack audit status is changed to Verified - Error, the audit status is changed to Completed With Error | Pass
9 | Manually create an audit, set a device to Absent | The device is changed to Absent status, the rack audit status is changed to Verified - Error, the audit status is changed to Completed With Error | Pass
10 | Manually create an audit, validate a rack with rackmount assets not validated | The rack cannot be validated before the rackmount devices are validated | Pass
11 | Manually create an audit, validate a rack with all rackmount assets validated | The rack is changed to Verified status | Pass
12 | Manually create an audit, validate a rack without devices mounted | The rack is changed to Verified status | Pass
13 | Manually create an audit, validate a blade | The blade is changed to Verified status
14 | Manually create an audit, create a blade |  | Failed | Cannot create new blades in MAM
15 | Manually create an audit, set a blade to Absent | The blade is changed to Absent status, the enclosure of the blade is changed to Verified - Error, the rack is changed to Verified - Error, the audit is changed to Completed With Error | Pass
16 | Manually create an audit for a validated rack | All devices and cables audit status are reset to Not Verified | Pass
17 | Edit rackmount assets in the audit (device name, rack U, SN, Asset Tag, Product Code) | The device name, rack U, SN, Asset Tag, Product Code are changed in VDC | Pass
18 | Delete rackmount assets in the audit | The rackmount device is removed from the rack | Pass | No logs for this operation
19 | Edit cables in the audit | The attributes on the cable is changed | Pass
20 | Delete cables in the audit | The cable is deleted on the device | Pass
21 | Validate SN, Asset Tag and Product Code in MAM failed | Validated with correct logs | Pass
22 | Validate SN, Asset Tag and Product Code in MAM succeeded | Validated with correct logs | Pass
23 | Validate SN, Asset Tag and Product Code in MAM and replace the value | Validated with correct logs, and the attributes are updated correctly in VDC and MAM | Pass
24 | Export devices with Audit Status | Audit status shows correct in the exported file | Pass
25 | Import devices with Audit Status | Import cannot change the value of audit status | Pass
26 | Install a server and generate audit with the WO, validate the reserved cables and device | The cables and device is changed to Verified status, the audit is changed to Completed status, the work order is changed to Completed status | Pass
27 | Move a server in same rack and generate audit with the WO, validate the reserved cables and device | The cables and device is changed to Verified status, the audit is changed to Completed status, the work order is changed to Completed status | Pass
28 | Move a server in a different rack and generate audit with the WO, validate the reserved cables and device | The cables and device is changed to Verified status, the audit is changed to Completed status, the work order is changed to Completed status | Pass
29 | Decommission a server and generate audit with the WO, validate the device | The device is changed to Verified status, the audit is changed to Completed status, the work order is changed to Completed status | Pass
30 | Install 3 racks and generate audit with the WO, validate the racks | When all racks are verified, the audit status is changed to Completed and the work order is completed | Pass
31 | Move 3 racks and generate audit with the WO, validate the racks | When all racks are verified, the audit status is changed to Completed and the work order is completed | Pass
32 | Decommission 3 racks and generate audit with the WO, validate the racks | When all racks are verified, the audit status is changed to Completed and the work order is completed | Pass
33 | Manually create an audit with a rack, then install a server in the rack and generate audit with the WO | In the manually created audit, the reserved device cannot be validated, when all mounted devices are verified, the rack can be validated | Pass
34 | Manually create an audit with a rack, then move a server in the rack and generate audit with the WO | In the manually created audit, the reserved device cannot be validated, when all mounted devices are verified, the rack can be validated | Pass
35 | Manually create an audit with a rack, then decommission a server in the rack and generate audit with the WO | In the manually created audit, the reserved device cannot be validated, when all mounted devices are verified, the rack can be validated | Pass